## FR10
Equipment Data Sheet
Fuel Oil Bulk Storage Tanks
FR120-ARP-GT-XX-SP-M-FUEL-8001
Job Title: |  | Equinix FR12.1 Frankfurt | [8 empty] | Date: |  | 2023-02-03
Job Number: |  | 285668-00 |  | Purpose of Issue: |  |  |  | D2 |  |  | Revision: |  | P02
Made by: |  | BP |  | Checked by: |  |  |  | DD
General Data
Unit Reference |  |  |  |  | 1FBULK_M1_1 1FBULK_M1_2 1FBULK_M1_3 1FBULK_M1_4 1FBULK_M1_5 1FBULK_M1_6 1FBULK_M1_7
Phase |  |  |  |  | Phase 1
Model Reference |  |  |  |  | BT TDM
Quantity Required |  |  |  |  | 7
Location
System |  |  |  |  | Fuel oil
Net Capacity per tank |  |  |  | litres | 85000
Type |  |  |  |  | Double skinned
Performance Data |  |  |  |  | Required |  | Offered | [5 empty] | Required |  | Offered
Fluid |  |  |  |  | Fuel oil - Diesel |  |  |  | Storage Temperature |  |  | °C | 5.5 - 40
Nominal Capacity per module |  |  |  | litres | n/a |  |  |  | Head Above Top of Tank |  |  | m
[9 empty] | Test Pressure |  |  | bar (g) | STA
Construction Data
Internal Tank Material |  |  |  |  | Steel |  |  |  | Outlet connection |  |  |  | DN80
Internal Tank Thickness |  |  |  |  | 9 |  |  |  | Return connection |  |  |  | DN65
Shell Material |  |  | (Note 11) |  | Steel |  |  |  | Fuel fill connection |  |  |  | DN65
Shell Thickness |  |  |  | mm | 4 |  |  |  | Vent connection size |  |  |  | 1xDN65
Type of Support |  |  |  |  | STA |  |  |  | Manhole Size (Ø) |  |  | mm | 600
Operating Weight |  |  |  | kg | STA |  |  |  | Level Indication Type
Weight Empty |  |  |  | kg | 14400
Dimensional Data
Tank Length |  |  |  | mm | 13250 |  |  |  | Front/Rear Access |  |  | mm | STA
Tank Dimension |  |  |  | mm | 2900 |  |  |  | Side Access |  |  | mm | STA
Tank Height |  |  |  | mm | 3000
Controls |  |  |  |  | Required |  | Offered |  |  | BMS Interface |  | Required |  | Offered
High-High Level Alarm Switch | [5 empty] | ü |  |  |  | Level Transmitter |  |  | ü
High Level Alarm Switch | [5 empty] | ü
Low Level Alarm Switch | [5 empty] | ü
Critical Low Level Alarm Switch | [5 empty] | ü
Pump Start Switch | [5 empty] | ü
BMS Links | [5 empty] | ü
Pump Panel Links | [5 empty] | ü
Accessories |  |  |  |  | Required |  | Offered |  |  |  |  | Required |  | Offered
Level Transmitters | [5 empty] | ü |  |  | Outlet Valve |  |  |  | ü
Calibrated Contents Gauge | [5 empty] | ü |  |  | Access Ladder |  |  |  | ü
Vent Pipe Pressure Relief Valve | [5 empty] | ü |  |  | Top Walkway |  |  |  | ü
Dished Ends | [5 empty] | ü |  |  | Handrail |  |  |  | ü
Fill Valve and switch | [5 empty] | ü |  |  | Access Hatch |  |  |  | ü
Overflow Screening | [5 empty] | ü |  |  | Sealed Heavy Duty Lid
Warning Pipe Screening | [8 empty] | Sealed Light Duty Lid
[9 empty] | Leak detection |  |  |  | ü
Testing |  |  |  |  | Required |  | Offered
Pressure Type Tests
Works Pressure Tests | [5 empty] | ü
Site OEM Pressure Tests | [5 empty] | ü
Manufacturer
Manufacturer |  |  |  |  | BTD
Contact Name |  |  |  |  | Jasmin Necker
Telephone Number |  |  |  |  | +49 (0) 71 57 5 62-175
Fax Number |  |  |  |  | +49 (0) 71 57 5 62-267
E-mail Address |  |  |  |  | j.necker@btd-gmbh.de
Internet Address |  |  |  |  | www.btd-gmbh.de
Additional Information
1 | This equipment data sheet must be read in conjunction | [7 empty] | 8 | Return pipe to tank mid-level.
with all other parts of the SoR, including:
| Fuel Description of Operation, layouts and schematics | [7 empty] | 9 | Pipe supports details which are connected to the Tank
container to be confirmed and agreed with manufacturer
2 | Drain points to tanks shall be from the top of the
| tank and shall be piped inside the tank to low level. | [7 empty] | 10 | Tanks and Fuel Oil Installation to be in accordance
with VAwS-Hessen, DIN EN 12285-1:2005-05, TRGS 509.
3 | Non-return valve required on outlet connection pipe.
[9 empty] | 11 | Tank design and contruction to be fully compliant with
4 | Stairs, platforms, etc provided as part of tank. | [8 empty] | FM Global design standards.
5 | Tank construction to be double wall with | [7 empty] | 13 Final pipework position to be confirmed with Tank
| Leak detection system in between | [8 empty] | manufacturer
6 | Fuel polishing connection / sampling branch to be located
at a lower level in the tank than the main supply branch.
7 | Vent to come complete with biofilter.