## FR12
Equipment Data Sheet
Fuel Oil Pumps
FR120-ARP-GT-XX-SP-M-FUEL-8002
Job Title: |  | Equinix FR12.1 Frankfurt | [9 empty] | Date: | 2023-02-03
Job Number: |  | 285668-0 | Purpose of Issue: |  |  |  |  | D2 |  |  |  | Revision: | P02
Made by: |  | BP | Checked by: |  |  |  |  | DD
General Data
Unit Reference |  |  |  |  | 1FP_M1R1_1 1FP_M1R1_2
Phase |  |  |  |  | Phase1
Model Reference |  |  |  |  | RD2A-B-2
Quantity |  |  |  |  | 2
Location |  |  |  |  | Fuel Pump Room 1, Fuel Pump Room 2
System |  |  |  |  | Fuel - Supply
Performance Data |  |  |  |  | Required |  | Offered
Diesel Oil Type |  |  |  |  | Heizöl EL
Flow Rate |  |  |  | kg/s | 6.05
Total Pump Pressure |  |  |  | bar (g) | 3.1
Minimum Flow Rate |  |  |  | kg/s | STA
Pressure @ Min Flow |  |  |  | kPa | STA
Pump Speed |  |  |  | rpm | 3000
Max Operating Temperature |  |  |  | °C | 40
Max Outlet Pressure |  |  |  | bar (g) | 10
Construction Data
Pump Type |  |  |  |  | Self Priming Centrifugal
Drive Type |  |  |  |  | VFD
Casing Material |  |  |  |  | Ductile Iron
Rotor Material |  |  |  |  | Copper Alloy
Shaft Material |  |  |  |  | Steel
Shaft Seal Type |  |  |  |  | Flurocarbo Elastomers, Carbon rotating face
Connection Type |  |  |  |  | Flange
Electrical Data |  |  |  |  | Required |  | Offered
Electrical Supply |  |  |  | V/Ø/Hz | 400/3/50
Drive Efficiency |  |  |  | % | STA
Motor Efficiency |  |  |  | % | STA
Absorbed Power |  |  |  | kW | 5.4
Motor Rating |  |  |  | kW | 7.5
Motor Speed |  |  |  | rpm | Variable
Starting Current |  |  |  | A | 69.5
Full Load Running Current |  |  |  | A | 8.2
Power Source |  |  |  |  | 3-phase /400 V, 50 Hz
Dimensional Data |  |  |  |  | Required |  | Offered
Suction Connection (Ø) |  |  |  | mm | 80
Discharge Connection (Ø) |  |  |  | mm | 50
Overall Length |  |  |  | mm | 505
Overall Width |  |  |  | mm | 420
Overall Height |  |  |  | mm | 420
Operating Weight |  |  |  | kg | STA
Mounting Method |  |  |  |  | STA
Accessories |  |  |  |  | Required |  | Offered
Anti Vibration Mountings | [5 empty] | ü
High Efficiency Motors | [5 empty] | ü
Motor Speed / Torque Curve | [5 empty] | ü
Variable Frequency Drive | [5 empty] | ü
BMS Outputs |  |  |  |  | Required |  | Offered |  |  | BMS Inputs |  |  | Required |  | Offered
Common Alarm - Volt Free Contact | [5 empty] | ü |  |  |  | Enable/Disable - Volt Free Contact |  |  |  | ü
Run Status - VFC | [5 empty] | ü |  |  |  | Set points |  |  |  | ü
Available | [5 empty] | ü
Testing |  |  |  |  | Required |  | Offered |  |  |  | Samples |  | Required |  | Offered
Performance Type Tests | [5 empty] | ü |  |  |  |  | Type Samples
Works Performance Tests | [5 empty] | ü
Site OEM Performance Tests | [5 empty] | ü
Manufacturer
Manufacturer |  |  |  |  | Gorman-Rupp Pumps
Contact Name |  |  |  |  | Matthew Zwaneveld
Telephone Number |  |  |  |  | +31 (0) 6-38172558
Fax Number |  |  |  |  | -
E-mail Address |  |  |  |  | matthew.zwaneveld@gormanrupp.com
Internet Address |  |  |  |  | GRpumps.eu
Additional Information | [8 empty] | Comments
1 | Pumps to be provided with VSD for constant speed control | [7 empty] | AVM - antivibration mount
and commissioning.
STA - supplier to advice
2 | Pumps to overcome project-specific pressure requirements on
the system's suction side (final figures to be determined by contractor)
3 | Pump shall come with vent pipe connection. Vent pipe to be
connected to fuel return line to bulk tanks (non-pressurized
line) or to be vented to the exterior
4 | Type test data shall be provided to demonstrate that
the equipment performs to the required standards.
5 | Submit pump curves to demonstrate operating point and
part load performance.
6 | Pumps shall be capable if operating in -10c entering fuel
temperature
7 | Fuel distribution system controls to be fully redundant
PLC type with no single point of failure (design of Controls
by BMS Contractor)
8 | The contractor is responsible to confirm the final pressure
drop of the pipework system installed, taking into account
changes made on site to the Detailed Design and reflect this
increased pressure drop in the final pump selection.