## FR12
Equipment Data Sheet
Fuel Valves
FR120-ARP-GT-XX-SP-M-FUEL-8003
Job Title: |  | Equinix FR12.1 Frankfurt | [9 empty] | Date: |  |  | 2023-02-03
Job Number: |  | 285668-00 | Purpose of Issue: |  |  |  | D2 |  |  |  |  | Revision: |  |  | P02
Made by: |  | BP | Checked by: |  |  |  | DD
Service |  |  |  | Fuel
Max Operating Pressure |  |  | bar (g) | 16 |  |  |  |  | Nominal Operating Temperature |  |  |  | °C | 20/32
System Test Pressure |  |  | bar (g) | [5 empty] | Max Operating Temperature |  |  |  | °C | 40
Application |  |  |  | Isolating |  |  |  | Isolating |  |  | PSV for Fuel system |  |  | Motorised Isolating
Type of Valve / Fitting |  |  |  | Butterfly valve |  |  |  | Butterfly valve |  |  | Spring loaded |  |  | Butterfly Valve
Size (DN) |  |  | mm | 15-50 |  |  |  | 65-100 |  |  | 65 |  |  | 65-100
Body Material |  |  |  | Cast Iron |  |  |  | Cast Iron |  |  | Cast Iron |  |  | Cast Iron
Trim Material |  |  |  | stainless steel |  |  |  | stainless steel |  |  | stainless steel |  |  | stainless steel
Connection Type |  |  |  | Flanged |  |  |  | Flanged |  |  | Flanged |  |  | Flanged
Model Reference
Preferred Manufacturer
Alternative Manufacturer
Further Comments | [7 empty] | see note 1 | [5 empty] | see note 4
Application |  |  |  | Non Return |  |  |  | Non Return |  |  | Strainer |  |  | Strainer
Type of Valve / Fitting |  |  |  | Swing Check Valve |  |  |  | Swing Check Valve |  |  | Y Type |  |  | Y Type
Size (DN) |  |  | mm | 15-50 |  |  |  | 65-100 |  |  | 15-50 |  |  | 65-100
Body Material |  |  |  | Bronze |  |  |  | Cast Iron |  |  | Malleable Iron |  |  | Cast Iron
Trim Material | [7 empty] | Stainless Steel
Connection Type |  |  |  | Screwed |  |  |  | Flanged |  |  | Screwed |  |  | Flanged
Model Reference
Preferred Manufacturer
Alternative Manufacturer
Further Comments
Application |  |  |  | Flow Regulation |  |  |  | Flow Regulation |  |  | Drain |  |  | Air Vent
Type of Valve / Fitting |  |  |  | Y Type FODRV |  |  |  | Y Type FODRV |  |  | Drain Cock |  |  | Globe Valve
Size (DN) |  |  | mm | 15-50 |  |  |  | 65-100 |  |  | 15-50 |  |  | 6-50
Body Material |  |  |  | Bronze |  |  |  | Cast Iron |  |  | Bronze |  |  | Malleable Iron
Trim Material | [7 empty] | Stainless Steel
Connection Type |  |  |  | Screwed |  |  |  | Flanged
Model Reference
Preferred Manufacturer
Alternative Manufacturer
Further Comments
Testing |  |  |  | Required |  | Offered |  |  |  | Samples |  |  |  | Required |  | Offered
Performance Type Tests |  |  |  |  | ü |  |  |  |  | Type Samples |  |  |  |  | ü
Manufacturer
Manufacturer |  |  |  | -
Contact Name |  |  |  | -
Telephone Number |  |  |  | -
Fax Number |  |  |  | -
E-mail Address |  |  |  | -
Internet Address |  |  |  | -
Additional Information | [8 empty] | Comments
1 | Isolating valves should fully lugged butterfly valves. | [8 empty] | PSV - pressure sustaining valve (back pressure regulating valve)
The disc and stem should be made of stainless steel
Seal material to be compatible with fluid
2 | All external valves are to be weather proved and suitable
for external installation
3 | For pipework configuration refer to schematic
FR120-ARP-GT-ZZ-SC-M-FUEL-6101
4 | Motorised valves to be interfaced with the fuel control panel
to enable selection of bulk tank for filling / supply / return