## FR10
Equipment Data Sheet
Fuel Meter
FR120-ARP-GT-XX-SP-M-FUEL-8004
Job Title: |  | Equinix FR12.1 Frankfurt | [17 empty] | Date: | 2023-02-03
Job Number: |  | 285668-0 |  |  |  |  | Puporse of Issue: | D2 | [11 empty] | Revision: | P03
Made by: |  | BP |  |  |  |  | Checked by: | DD
General Data | [7 empty] | Required |  | Offered
Unit Reference | [7 empty] | 1FM_1 1FM_2 1FM_3 1FM_4 1FM_5 1FM_6 1FM_7
Phase | [7 empty] | Phase 1
Quantity | [7 empty] | 7
Flow Meter Type Reference | [7 empty] | ProcessMaster
Transmitter Type Reference | [7 empty] | STA
System Type | [7 empty] | Diesel Oil
Meter Type | [7 empty] | Electromagnetic
Location | [7 empty] | Generators Building Internal for Bulk Tank Filling
Nominal Size | [6 empty] | DN | 65
AG
Accuracy | [5 empty] | % | Class | 0.4
Energy Accuracy Over Working Range | [6 empty] | ±% max | -
Minimum Length of Straight Pipe Upstream | [6 empty] | x DN | 5
Minimum Length of Straight Pipe Downstream | [6 empty] | x DN | 3
Maximum Admissible Temperature | [6 empty] | °C | 80
Limits of Temperature Range (Θmax/Θmin) | [6 empty] | °C | -10/70
Limits of Temperature Differences (ΔΘmax/ΔΘmin) | [6 empty] | °C | -
Operating pressure, absolute (minimum) | [6 empty] | bar (g) | 0.03 bar
Minimum Service Life | [6 empty] | hours
Environmental Class | [7 empty] | STA
IP Rating | [7 empty] | IP67
General Construction Data
Body Material | [7 empty] | STA
Mounting Arrangement
Connection Type | [7 empty] | Flange
Accessories
Data Logging Processor Unit | [8 empty] | ü
Temperature Sensors and Protection Pockets
Processor Unit | [17 empty] | Required |  | Offered
|  |  | Required |  | Offered |  |  | Required |  | Offered | Required | Offered |  |  | Memory Type
|  |  | Data Logged |  |  |  |  | Log Frequency |  |  | Log Period |  |  |  | Display Type |  |  | LCD
Energy |  | kWh | [12 empty] | Battery Type
Flow Rate |  | m3/hr | ü | [11 empty] | Battery Life |  | Hours
Flow Temperature |  | °C | [12 empty] | Interfaces
Return Temperature |  | °C | [12 empty] | Analogue (4-20mA) |  |  |  | ü
Volume |  | m3 | ü | [11 empty] | Digital
Hours Run |  | Hours | ü | [11 empty] | RS 232
Change Log | [14 empty] | Modbus |  |  |  | ü
Software Application |  |  | Required
Offered
Testing |  |  | Required |  | Offered | [5 empty] | Samples |  |  | Required |  | Offered
Performance Type Tests |  |  |  | ü | [6 empty] | Type Samples
Works Performance Tests
Site OEM Performance Tests
Manufacturer |  |  | Preferred |  |  |  |  | Alternative |  |  | Alternative
Flow Meter Type Reference |  |  | ProcessMaster DN65
Manufacturer |  |  | ABB
Contact Name
Telephone Number |  |  | +49 551 905 0
Fax Number |  |  | +49 551 905 777
E-mail Address |  |  | vertrieb.messtechnik-produkte@de.abb.com
Internet Address |  |  | abb.com/measurement
Additional Information | [12 empty] | Comments
1. | Fuel metering for emissions monitoring and reporting to RP Darmstadt to be provided as | [11 empty] | STA - Supplier To Advice
part of the generator MCE pack.