## Tanks
Equipment Data Sheet
AdBlue Bulk Storage Tank
FR120-ARP-GT-XX-SP-M-FUEL-8005
Job Title: |  | Equinix FR12.1 Frankfurt | [8 empty] | Date: |  | 2023-02-03
Job Number: |  | 285668-00 | Purpose of Issue: |  |  |  | D2 |  |  | Revision: |  |  | P02
Made by: |  | BP | Checked by: |  |  |  | DD
General Data
Unit Reference |  |  |  | 1ADBBULK_M1_1 1ADBBULK_M1_2
Phase |  |  |  | Phase 1
Model Reference |  |  |  | KTD - F- I - 2.5 - C
Quantity Required |  |  |  | 2
Location |  |  |  | AdBlue Room
System |  |  |  | AdBlue ®
Net Capacity |  |  | litres | 2670 (100% fill)
Type |  |  |  | Double skinned
Performance Data |  |  |  | Required |  | Offered | [6 empty] | Required |  | Offered
Fluid |  |  |  | AdBlue ® |  |  |  | Storage Temperature |  |  |  | °C | 5-40
Nominal Capacity |  |  | litres | 2510 |  |  |  | Head Above Top of Tank |  |  |  | m | N/A
[8 empty] | Test Pressure |  |  |  | bar (g) | STA
Construction Data
Arrangement |  |  |  | Rectangular stand alone |  |  |  | Outlet connection |  |  |  | mm | 32
Type of Construction |  |  |  | Steel |  |  |  | Return connection |  |  |  | mm | 32
Construction Standard | [7 empty] | Fuel fill connection
Shell Material |  |  |  | STA |  |  |  | Vent connection size
Shell Thickness |  |  |  | STA |  |  |  | Manhole Size (Ø) |  |  |  | mm | 600
Tank Plate Finish / Colour | [7 empty] | Level Indication Type
Type of Support |  |  |  | Steel pallet |  |  |  | Operating Weight |  |  |  | kg | 3500
[8 empty] | Weight Empty |  |  |  | kg | 980
Dimensional Data
Total Length |  |  | mm | 2000 |  |  |  | Front/Rear Access |  |  |  | mm
Total Width |  |  | mm | 1220 |  |  |  | Side Access |  |  |  | mm
Total Height |  |  | mm | 1850
Controls |  |  |  | Required |  | Offered |  |  | BMS Interface |  |  | Required |  | Offered
High-High Level Alarm Switch |  |  |  |  | ü |  |  |  | Level Transmitter |  |  |  | ü
High Level Alarm Switch |  |  |  |  | ü
Low Level Alarm Switch |  |  |  |  | ü
Low-Low Level Alarm Switch |  |  |  |  | ü
Pump Start Switch |  |  |  |  | ü
BMS Links |  |  |  |  | ü
Pump Panel Links |  |  |  |  | ü
Accessories |  |  |  | Required |  | Offered | [5 empty] | Required |  | Offered
Level Transmitters |  |  |  |  | ü |  |  | Outlet Valve |  |  |  |  | ü
Calibrated Contents Gauge |  |  |  |  | ü |  |  | Access Ladder
Vent Pipe Pressure Relief Valve |  |  |  |  | ü |  |  | Top Walkway
Dished Ends |  |  |  |  | ü |  |  | Handrail
Fill Valve and switch |  |  |  |  | ü |  |  | Access Hatch |  |  |  |  | ü
Overflow Screening | [7 empty] | Sealed Heavy Duty Lid
Warning Pipe Screening | [7 empty] | Sealed Light Duty Lid
[8 empty] | Leak detection |  |  |  |  | ü
Testing |  |  |  | Required |  | Offered |  | Samples |  |  |  | Required |  | Offered
Performance Type Tests
Works Pressure Tests |  |  |  |  | ü
Site OEM Performance Tests |  |  |  |  | ü
Manufacturer
Manufacturer |  |  |  | Krampitz Maschinentank GmbH
Contact Name
Telephone Number |  |  |  | (+49) 3901/3088-100
Fax Number |  |  |  | (+49) 3901/3088-131
E-mail Address |  |  |  | auftragsbearbeitung@krampitz.de
Internet Address |  |  |  | www.krampitz.de
Additional Information
1 | This equipment data sheet must be read in conjunction | [6 empty] | 6 | Tank construction to be double wall with
| with all other parts of the SoR, including: | [7 empty] | Leak detection system in between
layouts and schematics
[8 empty] | 7 | Tank and AdBlue Installation to be in accordance
2 | Drain points to tanks shall be from the top of the | [7 empty] | with VAwS-Hessen, DIN EN 12285-1:2005-05, TRGS 509.
tank and shall be piped inside the tank to low level.
[8 empty] | 8 | Tank design and contruction to be fully compliant with
3 | Non-return valve required on outlet connection pipe. | [7 empty] | FM Global design standards.
4 | Ladder, platforms, etc provided as part of tank. | [6 empty] | 9 | Final pipework position to be confirmed with Tank
manufacturer
5 | Vent to come complete with biofilter.
[8 empty] | 10 | Pipe supports details which are connected to the Tank
container to be confirmed and agreed with manufacturer
[8 empty] | 11 | Tank to be equipped with foot valve.