## FR12
Equipment Data Sheet
AdBlue Pumps
FR120-ARP-GT-XX-SP-M-FUEL-8006
Job Title: |  | Equinix FR12.1 Frankfurt | [10 empty] | Date: | 2023-02-03
Job Number: |  | 285668-00 | Purpose of Issue: |  |  |  |  | D2 |  |  |  | Revision: |  | P02
Made by: |  | BP | Checked by: |  |  |  |  | DD
General Data
Unit Reference |  |  |  |  | 1ADBP_M1_1
Phase |  |  |  |  | Phase 1
Model Reference |  |  |  |  | STA
Quantity |  |  |  |  | 1
Location |  |  |  |  | Internal
System |  |  |  |  | AdBlue ®
Type |  |  |  |  | STA
Speed Control |  |  |  |  | VSD
Performance Data |  |  |  |  | Required |  | Offered
Flow Rate |  |  |  | l/hr | 1020
Total Pump Pressure |  |  |  | bar (g) | 1.53
Minimum Flow Rate |  |  |  | kg/s | STA
Pressure @ Min Flow |  |  |  | kPa | STA
Inlet Pressure |  |  |  | bar (g) | -
Pump Efficiency |  |  |  | % | STA
Pump Speed (Note 1) |  |  |  | rpm | VSD
Max Operating Temperature |  |  |  | °C | 40
Max Outlet Pressure |  |  |  | bar (g) | -
NPSH Required |  |  |  | kPa | STA
Bearing Design Life |  |  |  | L10 Hrs | STA
Construction Data
Pump Type |  |  |  |  | Self-Priming Centrifugal
Configuration |  |  |  |  | In line
Drive Type |  |  |  |  | VSD
Casing Material |  |  |  |  | PP
Impeller Material |  |  |  |  | PP
Shaft Material |  |  |  |  | STA
Shaft Seal Type |  |  |  |  | STA
Casing & Base Finish / Colour |  |  |  | RAL | -
Connection Type |  |  |  |  | Flange
Electrical Data
Electrical Supply |  |  |  | V/Ø/Hz | 400/3/50
Drive Efficiency |  |  |  | % | STA
Motor Efficiency |  |  |  | % | STA
Absorbed Power |  |  |  | kW | STA
Motor Rating |  |  |  | kW | STA
Motor Type |  |  |  |  | STA
Motor Speed |  |  |  | rpm | STA
Starting Method |  |  |  |  | STA
Starting Current |  |  |  | A | STA
Full Load Running Current |  |  |  | A | STA
Power Source |  |  |  |  | electrical
Noise & Vibration Data
Anti Vibration Mount (AVM) Type |  |  |  |  | Rubber
Min AVM Static Deflection |  |  |  | mm | STA
Accessories |  |  |  |  | Required |  | Offered
Anti Vibration Mountings | [5 empty] | ü
High Efficiency Motors | [5 empty] | ü
Motor Speed / Torque Curve | [5 empty] | ü
BMS Outputs |  |  |  |  | Required |  | Offered |  |  | BMS Inputs |  |  |  |  | Required |  | Offered
Common Alarm - Volt Free Contact | [5 empty] | ü |  |  |  | Enable/Disable - Volt Free Contact | [5 empty] | ü
Run Status - VFC | [5 empty] | ü |  |  |  | Set points | [5 empty] | ü
Available | [5 empty] | ü
Testing |  |  |  |  | Required |  | Offered |  |  |  | Samples |  |  |  | Required |  | Offered
Performance Type Tests | [5 empty] | ü |  |  |  |  | Type Samples
Works Performance Tests | [5 empty] | ü
Site OEM Performance Tests | [5 empty] | ü
Manufacturer
Manufacturer |  |  |  |  | Steinle Indusutriepumpen |  |  |  | Sinntec Schmiersysteme GmbH
Contact Name
Telephone Number |  |  |  |  | (+49) 0211 / 30 20 55 10 |  |  |  | +49 (0) 5071 97903 0
Fax Number
E-mail Address |  |  |  |  | technik@steinle-pumpen.de |  |  |  | info@sinntec.de
Internet Address |  |  |  |  | www.steinle-pumpen.de |  |  |  | www.sinntec.de
Additional Information | [8 empty] | Comments
1 | Type test data shall be provided to demonstrate that | [7 empty] | AVM - antivibration mount
the equipment performs to the required standards.
STA - supplier to advice
2 | Submit pump curves to demonstrate operating point and
| part load performance. | [7 empty] | PP - Polypropylene
3 | The contractor is responsible to confirm the final pressure
| drop of the pipework system installed, taking into account | [7 empty] | Note
| changes made on site to the Detailed Design and reflect this | [7 empty] | 1 | VSD pump shall operate in constant speed
increased pressure drop in the final pump selection.
4 | Supplier to confirm that all gaskets are suitable for
AdBlue ® .
5 | Pump to be installed in storage tank enclosure for weather
protection.
6 | Pump to be controlled by external FU. External FU
to be included.
7 | Pump to be fully equipped with all flanges