## FR12
Equipment Data Sheet
Pipework
FR120-ARP-GT-XX-SP-M-FUEL-8008
Job Title: | Equinix FR12.1 Frankfurt | Puporse of Issue: | D2 |  |  | Date: | 2023-02-03
Job Number: | 285668-00 | Checked by: | DD |  |  | Revision: | P02
Made by: | BP
Service Code | Fluid | Pipe Code | Material | Max Press bar (g) | Max Operating Temp C |  | Notes
Fuel - Internal | Heizöl (Diesel) | BI | Carbon Steel | 16 | 45 |  | 1. All pipework not within bunded areas to be twin skinned with leak detection and drain points at low points
Fuel - External | Heizöl (Diesel) | BI | Stainless steel - Stainless steel - Polyethylen | 25 | 50 |  | Flexwell double wall pipework - three layers with vacuum leak detection
ADB - Internal | Adblue | PE | Stainless steel | 10 | 45 |  | 1. All pipework not within bunded areas to be twin skinned with leak detection and drain points at low points
ADB - External | Adblue | PE | Stainless steel - Stainless steel - Polyethylen | 25 | 50 |  | Flexwell double wall pipework - three layers with vacuum leak detection
Additional Information
1 This equipment data sheet must be read in conjunction with all other parts of the Specification and drawings.
2 Contractor to verify pipework expansion and make allowances for them. Any expansion provision to be fully compliant with
manufacturers requirement.